## Slide 1
FINAL PROJECT
ELECTRICAL SERVICES DESIGN LABORATORY
Presented By
  1806071 - Promit Biswas
  1806084 - KM Zulfikkar Sadik
  1806085 - Rudra Roy
  1806094 - Yeasmin Jahan Rima
  1806074 - Promit Ghosh
  1806083 - Emaz Elmi
Course No: EEE 414
ELECTRICAL SERVICES DESIGN PROJECT
Group: 05

## Slide 2
Introduction
We were instructed to model a three storied building having 2 units. Also, an instruction was to implement a parking & a basement having enough space. An elevator is also installed to ensure the ease of going any apartment without any time delay. Necessary safety managements have also been taken to ensure public safety

## Slide 3
Objectives
1. To get introduced to the floor-planning process of a typical multi-storied residential building.
2. To be familiarized with various fittings and fixtures utilized in each compartment of the building.
3. To get guidance on systematically drawing conduit layouts for the building.
4. To understand switchboard connections, including emergency setups.

## Slide 4
Design Steps
Ground floor and typical floor plan of a 3-storeyed building
Fittings and fixtures for each floor
Conduit layout planning for each floor
Switchboard and distribution board diagram

## Slide 5
Main Floor Plan

## Slide 6
Basement

## Slide 8
Our ground floor contains –
a. 1 Guard Room
b. Stair
c. 1 Toilet
d. Generator Room
e. MDB room
f. Transformer Room
g. Exit
Also, a lift is installed in Ground floor.
Ground Floor

## Slide 10
We have 2 units i.e. 2 apartments in each floor.
Every apartment consists of –
a. 1 Master Bedrooms
b. 2 Bedroom
c. 1 Living Room
d. 1 Dinning Space
e. 1 Kitchen
f. 3 Toilets
g. Free space as in Veranda
Also, a lift is installed in every floor
First Floor

## Slide 12
Floor Plan with Electrical Fittings

## Slide 16
Floor Plan with Conduit

## Slide 20
Roof Layout

## Slide 22
Distribution Board Circuit Diagram

## Slide 24
Sub Distribution Board

## Slide 25
Emergency Sub Distribution Board

## Slide 26
Sample Calculations
Light & Fan Calculation
Master Bedroom:
Area = 16’ x 11’-6”
= 184 ft2
= 17.094 m2
Let, Standard Luminance of the bedroom = 100 lux
Loss factor, LLf = 0.7 (assumed)
Utilization factor = 0.7 (as the bulb will be connected to wall)
We will use a 20W bulb which has standard luminance of 100 lux
So, Bulb needed = =
=1.953
So, we will use 1 20W LED bulb and 1 10W ceiling light bulbs.
Fan needed = = 1.84
So, 1 fan is needed.

## Slide 27
Power Calculation
Basement
For SB
Total load = 40 × 0.7 + 3000 × 0.2 = 628 Watt I=628/(220×0.7)=4.0779 A
∴2 × 1.5 rm BYM + 1.5 rm BYA ECC are used.
For SDB
Total load = 628 Watt
I=628/(220×0.7)=4.0779 A
∴2 × 1.5 rm BYM + 1.5 rm BYA ECC are used.
For ESB
Total load = 200 Watt
I=200/(220×0.7)=1.298 A
∴2 × 1.5 rm BYM + 1.5 rm BYA ECC are used.
For ESDB
Total load = 200 Watt
I=200/(220×0.7)=1.298 A
∴2 × 1.5 rm BYM + 1.5 rm BYA ECC are used.

## Slide 28
THANK YOU